## simple example
DC
DC
DC
DC
BESS
PV
AC
DC
DC
DC
Node 2
Node 1
Node 3
Node 4
Node 5
Node 6
Node 7
Node 11
Voltage level1
DC Load V1
Node 12
Node 0
DC
DC
Node 22
EV
Station
Node 21
Voltage level2
DC Load V2
DC Load V2
Node 20
Node 18
DC
DC
Node 9
DC
DC
Voltage level3
DC
AC
AC Load
DC Load V3
Node 13
Node 14
Node 15
Node 19
Node 16
Node 17
Node 23
Conv_1
Conv_1
Conv_2
Conv_3
Conv_4
Conv_5
Conv_6
Conv_7
Conv_8
DC Load V3
AC grid

## SLD Building
DC
DC
DC
DC
AC grid
BESS
PV
AC
DC
DC
DC
Z
Grid connection
Node 1
DC Bus
Node 101
DC
DC
Node 200
Node 2
Node 300
Node 3
Node 400
Node 4
Node 4XX
…
Voltage level1
DC Load V1
DC Load V1
Node 500
Node 5XX
Node 0
Node 450
Node 4XX+50
Node 10
Node 11
Node 100
…
DC
DC
DC
DC
…
Node 6
Node 9
EV
Station
Electrical board
Node 60
DC
DC
Voltage level2
…
DC Load V2
DC Load V2
Node 61
Node 6X
Node 6Y
Voltage level3
…
DC Load V3
DC Load V3
Node 601
Node 6XX
Node 600
DC
DC
Voltage level2
…
DC Load V2
DC Load V2
Node 91
Node 9X
Node 9Y
…
DC Load V3
DC Load V3
Node 901
Node 9XX
Node 900
Voltage level3

## Read me
Shift2DC EU
WP2 - DC Solutions Integration
Task T2.1 - Network Design Tool for DC Solutions
1. Excel file Overview
This Excel input file describes the grid topology and information for sizing and KPIs calculations.
It is designed to help you model a DC grid and its associated components systematically.
Remarks
This file contains multiple sheets described in section 2, each serving a specific purpose for grid description.
To ensure accurate modeling and reliable results, the user is invited to follow the instructions described in section 3.
2. Sheets description
Sheet Name | Purpose
Glossary | Define the parameters of all sheets.
UC Definition | Define project and use case details.
Assets Nodes | List all nodes in the grid with their associated assets.
Converters | List all converters in the grid.
Lines | List all lines in the grid.
3. Filling Guide
Step 1: Draw a Single Line Diagram (SLD)
It is crucial to prepare and organize your input data based on a well-defined SLD of the grid you want to study.
The SLD is a simplified representation of your DC grid, showing all key components and their interconnections.
Before proceeding to the input sheets of this file, draw your SLD on paper or digitally. Include the following:
a. Assets: DC loads, PV systems, storage systems, EV chargers, AC loads, and AC grids. |  | pending: add remarks about fillifn power values with signs (+ or -)
b. Lines: Indicate all DC cables connecting the assets.
c. Converters: Include all AC/DC converters, DC/AC converters, DC/DC converters (PDU, PV, Storage, EV).
d. Nodes: Mark and number each connection point (see step 2 below).
Step2: Add and Number Nodes to the Grid
Nodes are essential reference points in your grid for accurate modeling. Follow these rules for node placement:
i. On each asset: Assign a node number at each asset’s connection point (to the grid or to a converter).
ii. After each line: Place a node at the end of each line where it connects to another asset/component or line or converter.
iii. After each converter: Assign a node at the input and output of each converter.
Node Numbering Rules
Use consistent and sequential numbering across the grid.
Ensure every node in the SLD has a unique number.
Avoid reusing node identifiers.
Step 3: Fill the sheets using the SLD
Once your SLD is prepared and nodes are assigned, use it as a reference to fill the input sheets.
Step 3.a: Fill Sheet "UC Definition"
Provide project name, class, ecosystem, grid architecture details, and worst-case definitions.
Step 3.a: Fill Sheet "Assets Nodes"
Provide node number, asset type, operating voltage, power, capacity, associated converter.
Step 3.c: Fill Sheet "Converters"
Define converter types, nodes, nominal power, voltage level, efficiency, voltage control mode, and droop curve.
Step 3.d: Fill Sheet "Lines"
Provide line connections (starting and ending node), length, and section.
Key considerations
The node numbers in your sheets must match those in your SLD. Double-check your SLD and input sheets to avoid discrepancies.
Use the "Input Requirement" column in the "Glossary" sheet to identify which parameters are Mandatory, Optional, or Conditional.
Summary
Start with a clear and well-defined SLD.
Add nodes consistently at every asset, line, and converter.
Use the SLD to fill the sheets accurately, ensuring all nodes and parameters match.
Follow the input requirements to complete the data for the simulation.

## Glossary
Parameters description
Sheet Name | Parameter | Description | Value (if relevant) | Comment/Instruction | Input Requirement | Unit (if relevant)
UC Definition | Project name | Name of the project for identification |  | Enter the name of the project | Mandatory
UC Definition | Use case | Purpose of the project | Local consumption maximization | Select of one the listed purposes that matches the project | Mandatory
Resilience
UC Definition | Project class | Classification of the project/application | Commercial | Select one of the listed classfications | Mandatory
Industrial
Port
Residential
UC Definition | Ecosystem | Ecosystem type impacting volt control mode, voltage drop and voltage levels | CurrentOS | Select the relevant ecosystem | Mandatory
Open DC Alliance (ODCA)
UC Definition | Poles | Grid architecture type | Unipolar | Select the grid architecture type | Mandatory
Bipolar
Meshed
UC Definition | Total PV power installed (kW) |  |  |  | Optional | kW
UC Definition | Total EV charging station size (kW) |  |  |  | Optional | kW
UC Definition | Number of voltage levels | Number of voltage levels |  | Specify the number of voltage levels in the grid | Optional
UC Definition | Number of AC/DC converters | Number of AC/DC converters |  | Provide the number of AC/DC converters used | Optional
UC Definition | Number of DC/AC converters | Number of DC/AC converters |  | Provide the number of DC/AC converters used | Optional
UC Definition | Number of PDU DC/DC converters | Number of PDU DC/DC converters |  | Provide the number of PDU DC/DC converters used | Optional
UC Definition | Number of PV DC/DC converters | Number of PV DC/DC converters |  | Provide the number of PV DC/DC converters used | Optional
UC Definition | Number of storage DC/DC converters | Number of storage DC/DC converters |  | Provide the number of storage DC/DC converters used | Optional
UC Definition | Number of EV DC/DC converters | Number of EV DC/DC converters |  | Provide the number of EV DC/DC converters used | Optional
UC Definition | Operating temperature (degrees Celsius) | Operating temperature of the system |  | Specify the operation temperature | Mandatory | °C
UC Definition | Material | Conductor material | Aluminium (Al) | Choose the conductor material type | Mandatory
Copper (Cu)
UC Definition | Isolation | Conductor isolation type | PolyVinyl Chloride (PVC) | Choose the conductor isolation type | Mandatory
Cross-linked polyethylene (XLPE)
UC Definition | Cable sizing security factor (%) | Security factor for cable sizing |  | Specify the security factor in percentage | Mandatory | %
UC Definition | Cable sizing expansion factor (%) | Expansion factor for cable sizing |  | Specify the expansion factor in percentage | Mandatory | %
UC Definition | AC/DC converter sizing security factor (%) | Security factor for AC/DC converter sizing |  | Specify the security factor in percentage | Mandatory | %
UC Definition | Other converters sizing security factor (%) | Security factor for other converters (DC/AC, PDU DC/DC, PV DC/DC, Storage DC/DC, and EV DC/DC) sizing |  | Specify the security factor in percentage | Mandatory | %
UC Definition | All converters SSCB loss consideration | Whether all converters SSCB losses are considered or not | Yes | Select "Yes" if SSCB losses are considered | Mandatory
|  |  | No | Select "No" if SSCB losses are not considered
UC Definition
Assets Nodes | Component type | Type of asset | DC Load | Choose the asset type | Mandatory
PV
Storage
EV
AC Load
AC Grid
Assets Nodes | Node number | Unique identifier for the node |  | Assign a unique identifier to each node of the grid | Mandatory
Assets Nodes | Node type | Node type, modeling for the load flow | V | Choose V for the assets "AC grid" | Mandatory
|  |  | P | Choose P for the assets "DC load", "AC load"
|  |  | storage | Choose storage for the assets "Storage", "EV"
|  |  | gen | Choose gen for the asset "PV"
Assets Nodes | Operating nominal voltage | Operating nominal voltage of the node |  | Specify the voltage level for all node types | Mandatory | V
Assets Nodes | Maximum Power | Maximum power consumed/generated |  | Specify the maximum power in kilowatts if the node type is P, storage or gen, otherwise leave empty | Conditional (on node type) | kW
Assets Nodes | Capacity | Capacity value |  | Specify the storage capacity in kilowatt-hours if the node type is storage, otherwise leave empty | Conditional (on node type) | kWh
Assets Nodes | Associated converter name | Name of the converter associated with the node |  | Provide the name of the converter: Conv_X where X∈[1,m], with m=total number of converters in the grid | Mandatory
Assets Nodes | Node number for associated converter | Unique identifier for the converter associated with the node |  | Assign a unique identifier to each converter | Mandatory
Assets Nodes | Daily/Annual curve type
Converters | Converter name | Name of the converter associated with the node |  | Provide the name of the converter: Conv_X where X∈[1,m], with m=total number of converters in the grid | Mandatory
Converters | Node_i number | Unique identifier for the starting node of the converter connection |  | Specify the asset-side or lower voltage bus side starting node | Mandatory
Converters | Node_j number | Unique identifier for the ending node of the converter connection |  | Specify the DC grid-side or higher voltage bus side ending node | Mandatory
Converters | Converter type | Converter type | AC/DC Converter Isolated | Select the converter type | Mandatory
AC/DC Converter Non-Isolated
DC/AC Converter
PDU DC/DC Converter Isolated
PDU DC/DC Converter Non-Isolated
PV DC/DC Converter
Storage DC/DC Converter
EV DC/DC Converter
Converters | Voltage level V_i (V) | Voltage level for the starting node of the converter connection |  | Specify the voltage level on the asset side or lower voltage bus | Conditional (on converter type) | V
Converters | Voltage level V_j (V) | Voltage level for the ending node of the converter connection |  | Specify the voltage level on the DC grid side or higher voltage bus | Conditional (on converter type) | V
Converters | Nominal power (kW) | Nominal power of the converter |  | Specify the nominal power of the converter if already sized/fixed, otherwise the tool will determine the nomial power of the converter | Optional | kW
Converters | Efficiency curve | Efficiency curve of the converter | default | Choose "default" for a constructor default efficiency curve per converter type | Mandatory
|  |  | user-defined | Choose "user-defined" for a user-defined efficiency curve
Converters | Efficiency curve if user-defined | User-defined efficiency curve |  | Specify the efficiency curve, if "user-defined" is chosen, as follows: [Xi;Yi], i={1,2,3,4}, with X= Factor of Nominal Power (%), Y=Efficiency (%) | Conditional (on efficiency curve type)
Converters | Voltage control mode | Voltage control strategy for the converter | master-slave control | Choose the appropriate voltage control mode for each converter | Mandatory
droop control
Converters | Droop curve | Droop curve of the converter | default non-dynamic | Choose "default non-dynamic" for a default non-dynamic droop curve per converter type | Mandatory
|  |  | default dynamic | Choose "default dynamic" for a default dynamic droop curve per converter type
|  |  | user-defined non-dynamic | Choose "user-defined non-dynamic" for a user-defined non-dynamic droop curve
|  |  | user-defined dynamic | Choose "user-defined dynamic" for a user-defined dynamic droop curve
Converters | Droop curve if user-defined | User-defined droop curve |  | Specify the droop curve, if "user-defined" is chosen, as follows: [Vi;Pi], i={1,2,3,4,5,6}, with V=Asset voltage value (p.u.), P=Asset power value (p.u.) | Conditional (on efficiency curve type)
Lines | Node_i number | Unique identifier for the starting node of the line |  | Specify the starting node of the line connection | Mandatory
Lines | Node_j number | Unique identifier for the ending node of the line |  | Specify the ending node of the line connection | Mandatory
Lines | Line length | Length of the line connecting node i and node j |  | Specify the length of the line connecting Node_i and Node_j in meters | Mandatory | meter
Lines | Cable section | User predefined section of the cable |  | Specify the cross-sectional area of the cable in square millimeters if already sized, otherwise the tool will determine the section of each cable | Optional | mm²
Note on F25: [Commentaire à thread] Votre version d’Excel vous permet de lire ce commentaire à thread. Toutefois, les modifications qui y sont apportées seront supprimées si le fichier est ouvert dans une version plus récente d’Excel. En savoir plus : https://go.microsoft.com/fwlink/?linkid=870924 Commentaire : Check with Nexans team if we can add some recommendation for the user
Note on F27: [Commentaire à thread] Votre version d’Excel vous permet de lire ce commentaire à thread. Toutefois, les modifications qui y sont apportées seront supprimées si le fichier est ouvert dans une version plus récente d’Excel. En savoir plus : https://go.microsoft.com/fwlink/?linkid=870924 Commentaire : Check with Nexans team if we can add some recommendation for the user

## UC Definition
Project details
Project name | TEST
Use case | Local consumption maximization
Project domain | Residential
Ecosystem | ODCA
Grid architecture and inputs
Poles | Unipolar
Total PV power installed (kW)
Total EV charging station size (kW)
Number of voltage levels | 3
Number of AC/DC converters | 1
Number of DC/AC converters | 1
Number of PDU DC/DC converters | 2
Number of PV DC/DC converters | 1
Number of storage DC/DC converters | 1
Number of EV DC/DC converters | 2
Conductor parameters
Operating temperature (degrees Celsius) | 20
Material | Copper (Cu)
Isolation | PolyVinyl Chloride (PVC)
Cable sizing security factor (%) | 10
Cable sizing expansion factor (%)
Converter details
AC/DC converter sizing security factor (%) | 10
Other converters sizing security factor (%) | 5
All converters SSCB loss consideration | No
Worst case definition for Storage DC/DC converter sizing
Loads power factor (%) | 80
PV power (%) | 10
EV Charging station consumption (%) | 80
AC Grid (%) | 0
Worst case definition for AC/DC, DC/AC, PDU DC/DC, PV DC/DC and EV DC/DC converters sizing
Loads power factor (%) | 80
PV power (%) | 10
EV Charging station consumption (%) | 80
Storage power contribution (%) | 0
Note on A25: [Commentaire à thread] Votre version d’Excel vous permet de lire ce commentaire à thread. Toutefois, les modifications qui y sont apportées seront supprimées si le fichier est ouvert dans une version plus récente d’Excel. En savoir plus : https://go.microsoft.com/fwlink/?linkid=870924 Commentaire : foisonnement
Note on A32: [Commentaire à thread] Votre version d’Excel vous permet de lire ce commentaire à thread. Toutefois, les modifications qui y sont apportées seront supprimées si le fichier est ouvert dans une version plus récente d’Excel. En savoir plus : https://go.microsoft.com/fwlink/?linkid=870924 Commentaire : Instead of only AC/DC converter

## Assets Nodes
Component type | Node type | Node number | Operating nominal voltage (V) | Maximum power (kW) | Capacity (kWh) | Directly linked converter Conv_X | Node number for directly linked converter | Daily/Annual curve type
AC Grid | V | 0 | 400 |  |  | Conv_1 | 1
PV | P | 3 | 700 | 10 |  | Conv_2 | 4
Storage | storage | 5 | 700 | 30 | 1000 | Conv_3 | 6
EV | storage | 7 | 700 | 11 |  | Conv_4 | 11
EV | storage | 9 | 700 | 11 |  | Conv_5 | 11
DC Load | P | 12 | 700 | 2
AC Load | P | 13 | 400 | 2 |  | Conv_6 | 23
DC Load | P | 14 | 48 | 0.2
DC Load | P | 15 | 48 | 0.1
DC Load | P | 18 | 350 | 0.3
DC Load | P | 19 | 350 | 10
DC Load | P | 20 | 350 | 6

## Converters
Converter name | Node_i number Asset side / Lower Voltage Bus side | Node_j number DC Grid side / Higher Voltage Bus side | Converter type | Voltage level V_i (V) Asset side / Lower Voltage Bus side | Voltage level V_j(V) DC Grid side / Higher Voltage Bus side | Nominal power (kW) | Efficiency curve | Efficiency curve if user-efined [Xi;Yi], i={1,2,3,4}, with X= Factor of Nominal Power (%), Y=Efficiency (%) | Voltage control mode | Droop curve | Droop curve if user-efined [Vi;Pi], i={1,2,3,4,5,6}, with V=Asset voltage value (p.u.), P=Asset power value (p.u.)
Conv_1 | 0 | 1 | AC/DC Converter Non-Isolated | 400 | 700 | 10000 | user-defined | [[0,100],[50,98],[75,97],[100,95]] | master-slave control | user-defined non-dynamic | [[0,100],[50,98],[75,97],[100,95]]
Conv_2 | 3 | 4 | PV DC/DC Converter |  | 700 |  | default | [[0,100],[50,98],[75,97],[100,95]] | master-slave control | default non-dynamic
Conv_3 | 5 | 6 | Storage DC/DC Converter |  | 700 |  | default | [[0,100],[50,98],[75,97],[100,95]] | master-slave control | default non-dynamic
Conv_4 | 7 | 11 | EV DC/DC Converter |  | 700 |  | default | [[0,100],[50,98],[75,97],[100,95]] | master-slave control | default non-dynamic
Conv_5 | 9 | 11 | EV DC/DC Converter |  | 700 |  | default | [[0,100],[50,98],[75,97],[100,95]] | master-slave control | default non-dynamic
Conv_6 | 13 | 23 | DC/AC Converter |  | 700 |  | default | [[0,100],[50,98],[75,97],[100,95]] | master-slave control | default non-dynamic
Conv_7 | 16 | 17 | PDU DC/DC Converter Non-Isolated | 48 | 350 |  | default | [[0,100],[50,98],[75,97],[100,95]] | master-slave control | default non-dynamic
Conv_8 | 21 | 22 | PDU DC/DC Converter Non-Isolated | 350 | 700 |  | default | [[0,100],[50,98],[75,97],[100,95]] | master-slave control | default non-dynamic
Note on D1: [Commentaire à thread] Votre version d’Excel vous permet de lire ce commentaire à thread. Toutefois, les modifications qui y sont apportées seront supprimées si le fichier est ouvert dans une version plus récente d’Excel. En savoir plus : https://go.microsoft.com/fwlink/?linkid=870924 Commentaire : ILC, PDU, Asset converter (load, EV , Sto, PV), AC load Réponse : C'est important pour les courbes de droop
Note on G1: [Commentaire à thread] Votre version d’Excel vous permet de lire ce commentaire à thread. Toutefois, les modifications qui y sont apportées seront supprimées si le fichier est ouvert dans une version plus récente d’Excel. En savoir plus : https://go.microsoft.com/fwlink/?linkid=870924 Commentaire : Information non obligatoire p-e mettre des couleurs différentes ?

## Lines
Node_i | Node_j | Line length (m) | Cable section (mm²)
1 | 2 | 100
2 | 4 | 100
2 | 6 | 100
2 | 11 | 100
2 | 12 | 100
2 | 23 | 100
2 | 22 | 100
15 | 16 | 100
17 | 21 | 100
18 | 21 | 100
19 | 20 | 1
20 | 21 | 1
14 | 16 | 100
Note on D1: [Commentaire à thread] Votre version d’Excel vous permet de lire ce commentaire à thread. Toutefois, les modifications qui y sont apportées seront supprimées si le fichier est ouvert dans une version plus récente d’Excel. En savoir plus : https://go.microsoft.com/fwlink/?linkid=870924 Commentaire : Non utile pour moi

## Droop curves
Index Curve | 0 | 1 | 2 | 3 | 4
Converter type | Default Droop curve [Vi;Pi], i={1,2,3,4,5,6}, with V=Asset voltage value (p.u.), P=Asset power value (p.u.) | Droop curve [Vi;Pi], i={1,2,3,4,5,6} | Droop curve [Vi;Pi], i={1,2,3,4,5,6} | Droop curve [Vi;Pi], i={1,2,3,4,5,6} | Droop curve [Vi;Pi], i={1,2,3,4,5,6}
AC/DC Converter Non-Isolated | [1.085; 0], [1; 1], [1; 1], [1; 1], [1; 1], [0.915; 1]
PV DC/DC Converter | [1.085; 0], [1; 1], [1; 1], [1; 1], [1; 1], [0.915; 1]
Storage DC/DC Converter | [1.085; 0], [1; 1], [1; 1], [1; 1], [1; 1], [0.915; 1]
EV DC/DC Converter | [1.085; 0], [1; 1], [1; 1], [1; 1], [1; 1], [0.915; 1]
EV DC/DC Converter | [1.085; 0], [1; 1], [1; 1], [1; 1], [1; 1], [0.915; 1]
DC/AC Converter | [1.085; 0], [1; 1], [1; 1], [1; 1], [1; 1], [0.915; 1]
PDU DC/DC Converter Non-Isolated | [1.085; 0], [1; 1], [1; 1], [1; 1], [1; 1], [0.915; 1]
PDU DC/DC Converter Non-Isolated | [1.085; 0], [1; 1], [1; 1], [1; 1], [1; 1], [0.915; 1]