## bus
| name | vn_kv | type | zone | in_service
0 | Bus 0 | 0.4 | b |  | TRUE
1 | Bus 1 | 0.7 | b |  | TRUE
2 | Bus 2.0 | 0.7 | b |  | TRUE
4 | Bus 4 | 0.7 | b |  | TRUE
6 | Bus 6 | 0.7 | b |  | TRUE
8 | Bus 8 | 0.7 | b |  | TRUE
11 | Bus 11 | 0.7 | b |  | TRUE
19 | Bus 19 | 0.7 | b |  | TRUE
21 | Bus 21 | 0.7 | b |  | TRUE
3 | Bus 3 | 0.7 | b |  | TRUE
5 | Bus 5 | 0.7 | b |  | TRUE
7 | Bus 7 | 0.7 | b |  | TRUE
9 | Bus 9 | 0.7 | b |  | TRUE
10 | Bus 10 | 0.7 | b |  | TRUE
12 | Bus 12 | 0.048 | b |  | TRUE
17 | Bus 17 | 0.35 | b |  | TRUE
18 | Bus 18 | 0.35 | b |  | TRUE
20 | Bus 20 | 0.35 | b |  | TRUE
13 | Bus 13 | 0.35 | b |  | TRUE
15 | Bus 15 | 0.35 | b |  | TRUE
14 | Bus 14 | 0.048 | b |  | TRUE
16 | Bus 16 | 0.048 | b |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type | droop_curve | p_nom_mw | power_profile | default_power_profile
4 | load 21 | 21 | 0.002 | 0 | 0 | 0 |  | 1 | TRUE | wye |  | 0.002 | [0. 0. 0. 0. 0. 0. 0. 0.1 0.2 0.5 0.7 0.8 0.9 1. 0.9 0.8 0.7 0.5 0.2 0.1 0. 0. 0. 0. 0. 0. 0. 0. 0. 0. 0. 0.1 0.2 0.5 0.7 0.8 0.9 1. 0.9 0.8 0.7 0.5 0.2 0.1 0. 0. 0. 0. ]
11 | load 12 | 12 | 0.0005 | 0 | 0 | 0 |  | 1 | TRUE | wye | [[1.025 1. ] [1.05 1. ] [1. 1. ] [1. 1. ] [0.985 1. ] [0.975 0. ]] | 0.0005 | [0.3 0.3 0.3 0.3 0.3 0.3 0.3 0.3 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.3 0.3 0.3 0.3 0.3 0.3 0.3 0.3 0.3 0.3 0.3 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.9 0.3 0.3 0.3]
3 | load 20 | 20 | 0.001 | 0 | 0 | 0 |  | 1 | TRUE | wye |  | 0.001 | [0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.3 0.5 0.7 0.8 0.8 0.8 0.3 0.3 0.8 0.8 0.8 0.7 0.6 0.2 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.3 0.5 0.7 0.8 0.8 0.8 0.3 0.3 0.8 0.8 0.8 0.7 0.6 0.2 0.1 0.1 0.1]
1 | load 14 | 14 | 0.0005 | 0 | 0 | 0 |  | 1 | TRUE | wye | [[1.025 1. ] [1.05 1. ] [1. 1. ] [1. 1. ] [0.985 1. ] [0.975 0. ]] | 0.0005 | [0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.3 0.5 0.7 0.8 0.8 0.8 0.3 0.3 0.8 0.8 0.8 0.7 0.6 0.2 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.3 0.5 0.7 0.8 0.8 0.8 0.3 0.3 0.8 0.8 0.8 0.7 0.6 0.2 0.1 0.1 0.1]
2 | load 16 | 16 | 0.0005 | 0 | 0 | 0 |  | 1 | TRUE | wye | [[1.025 1. ] [1.05 1. ] [1. 1. ] [1. 1. ] [0.985 1. ] [0.975 0. ]] | 0.0005 | [0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.3 0.5 0.7 0.8 0.8 0.8 0.3 0.3 0.8 0.8 0.8 0.7 0.6 0.2 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.3 0.5 0.7 0.8 0.8 0.8 0.3 0.3 0.8 0.8 0.8 0.7 0.6 0.2 0.1 0.1 0.1]

## sgen
| name | bus | p_mw | q_mvar | sn_mva | scaling | in_service | type | current_source | p_nom_mw | power_profile | default_power_profile
0 | PV 9 | 9 | 0.03 | 0 |  | 1 | TRUE | wye | TRUE | 0.03 | [0. 0. 0. 0. 0. 0. 0. 0.1 0.2 0.5 0.7 0.8 0.9 1. 0.9 0.8 0.7 0.5 0.2 0.1 0. 0. 0. 0. 0. 0. 0. 0. 0. 0. 0. 0.1 0.2 0.5 0.7 0.8 0.9 1. 0.9 0.8 0.7 0.5 0.2 0.1 0. 0. 0. 0. ]
1 | PV 10 | 10 | 0.03 | 0 |  | 1 | TRUE | wye | TRUE | 0.03 | [0. 0. 0. 0. 0. 0. 0. 0.1 0.2 0.5 0.7 0.8 0.9 1. 0.9 0.8 0.7 0.5 0.2 0.1 0. 0. 0. 0. 0. 0. 0. 0. 0. 0. 0. 0.1 0.2 0.5 0.7 0.8 0.9 1. 0.9 0.8 0.7 0.5 0.2 0.1 0. 0. 0. 0. ]

## storage
| name | bus | p_mw | q_mvar | sn_mva | soc_percent | min_e_mwh | max_e_mwh | scaling | in_service | type | p_nom_mw | power_profile | default_power_profile
0 | Battery 3 | 3 | 0 | 0 |  | 50 | 0 | 0.12 | 1 | TRUE |  | 0.03
1 | EV 5 | 5 | 0.011 | 0 |  | 100 | 0 | 0.044 | 1 | TRUE |  | 0.011 | [0.1 0.1 0.1 0.1 0.1 0.1 0.3 0.3 0.9 0.85 0.8 0.75 0.7 0.3 0.2 0.75 0.7 0.65 0.6 0.5 0.2 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.3 0.3 0.9 0.85 0.8 0.75 0.7 0.3 0.2 0.75 0.7 0.65 0.6 0.5 0.2 0.1 0.1 0.1 ]
2 | EV 7 | 7 | 0.022 | 0 |  | 100 | 0 | 0.088 | 1 | TRUE |  | 0.022 | [0.1 0.1 0.1 0.1 0.1 0.1 0.3 0.3 0.9 0.85 0.8 0.75 0.7 0.3 0.2 0.75 0.7 0.65 0.6 0.5 0.2 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.1 0.3 0.3 0.9 0.85 0.8 0.75 0.7 0.3 0.2 0.75 0.7 0.65 0.6 0.5 0.2 0.1 0.1 0.1 ]

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | cable_rank | section
0 |  |  | 1 | 2 | 0.01 | 18.1 | 1e-20 | 0 | 0 | 0.027812 | 1 | 1 |  | TRUE | 2 | 1
1 |  |  | 2 | 4 | 0.02 | 12.1 | 1e-20 | 0 | 0 | 0.034015 | 1 | 1 |  | TRUE | 3 | 1.5
2 |  |  | 2 | 6 | 0.05 | 36 | 1e-20 | 0 | 0 | 0.01972 | 1 | 1 |  | TRUE | 0 | 0.5
3 |  |  | 2 | 8 | 0.05 | 18.1 | 1e-20 | 0 | 0 | 0.027812 | 1 | 1 |  | TRUE | 2 | 1
4 |  |  | 2 | 11 | 0.1 | 4.61 | 1e-20 | 0 | 0 | 0.055108 | 1 | 1 |  | TRUE | 5 | 4
5 |  |  | 2 | 19 | 0.01 | 36 | 1e-20 | 0 | 0 | 0.01972 | 1 | 1 |  | TRUE | 0 | 0.5
6 |  |  | 2 | 21 | 0.01 | 36 | 1e-20 | 0 | 0 | 0.01972 | 1 | 1 |  | TRUE | 0 | 0.5
7 |  |  | 13 | 18 | 0.005 | 36 | 1e-20 | 0 | 0 | 0.01972 | 1 | 1 |  | TRUE | 0 | 0.5
8 |  |  | 15 | 18 | 0.005 | 36 | 1e-20 | 0 | 0 | 0.01972 | 1 | 1 |  | TRUE | 0 | 0.5
9 |  |  | 17 | 18 | 0.005 | 36 | 1e-20 | 0 | 0 | 0.01972 | 1 | 1 |  | TRUE | 0 | 0.5
10 |  |  | 20 | 18 | 0.005 | 36 | 1e-20 | 0 | 0 | 0.01972 | 1 | 1 |  | TRUE | 0 | 0.5

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.0092771 | 0
1 | 1 | 0 | 0.010874 | -6.8323e-24
2 | 1.004 | 2.7066e-22 | 0 | 0
4 | 1.0038 | 2.5906e-22 | 0.0005 | 0
6 | 0.95888 | -4.4484e-22 | 0.011782 | 0
8 | 0.95963 | -1.1289e-21 | 0.023064 | 0
11 | 1.0553 | 6.6165e-21 | -0.0575 | 0
19 | 1.0005 | 2.1477e-22 | 0.0048014 | 0
21 | 1.0026 | 2.4743e-22 | 0.002 | 0
3 | 1 | 0 | 0 | 0
5 | 1 | 0 | 0.011 | 0
7 | 1 | 0 | 0.022 | 0
9 | 1 | 0 | 0.03 | 0
10 | 1 | 0 | 0.03 | 0
12 | 1 | 0 | 0.0005 | 0
17 | 0.99847 | -2.4303e-23 | 0.0010376 | 0
18 | 1 | 0 | -0.0041191 | -1.7318e-27
20 | 0.99853 | -2.342e-23 | 0.001 | 0
13 | 0.99847 | -2.4303e-23 | 0.0010376 | 0
15 | 0.99847 | -2.4303e-23 | 0.0010376 | 0
14 | 1 | 0 | 0.0005 | 0
16 | 1 | 0 | 0.0005 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010874 | 6.8323e-24 | 0.010918 | -6.8082e-24 | 4.3678e-05 | 2.4132e-26 | 0.0089688 | 0.0089688 | 0.0089688 | 1 | 0 | 1.004 | 2.7066e-22 | 32.2485
1 | 0.00050012 | 1.0128e-28 | -0.0005 | -9.5991e-35 | 1.2254e-07 | 1.0128e-28 | 0.00041084 | 0.00041084 | 0.00041084 | 1.004 | 2.7066e-22 | 1.0038 | 2.5906e-22 | 1.2078
2 | 0.012337 | 1.5406e-25 | -0.011782 | 4.6996e-33 | 0.00055461 | 1.5406e-25 | 0.010134 | 0.010134 | 0.010134 | 1.004 | 2.7066e-22 | 0.95888 | -4.4484e-22 | 51.3908
3 | 0.024131 | 5.8944e-25 | -0.023064 | 1.6959e-32 | 0.0010669 | 5.8944e-25 | 0.019823 | 0.019823 | 0.019823 | 1.004 | 2.7066e-22 | 0.95963 | -1.1289e-21 | 71.2772
4 | -0.054707 | 6.059e-24 | 0.0575 | 6.5036e-31 | 0.0027932 | 6.059e-24 | 0.044941 | 0.044941 | 0.044941 | 1.004 | 2.7066e-22 | 1.0553 | 6.6165e-21 | 81.5508
5 | 0.0048183 | 4.7002e-27 | -0.0048014 | -2.6267e-34 | 1.6921e-05 | 4.7002e-27 | 0.0039582 | 0.0039582 | 0.0039582 | 1.004 | 2.7066e-22 | 1.0005 | 2.1477e-22 | 20.0716
6 | 0.0020029 | 8.1218e-28 | -0.002 | -1.2175e-34 | 2.9238e-06 | 8.1218e-28 | 0.0016454 | 0.0016454 | 0.0016454 | 1.004 | 2.7066e-22 | 1.0026 | 2.4743e-22 | 8.3436
7 | -0.0010376 | 1.0247e-33 | 0.0010392 | 4.4081e-28 | 1.5869e-06 | 4.4081e-28 | 0.0017143 | 0.0017143 | 0.0017143 | 0.99847 | -2.4303e-23 | 1 | 0 | 8.6929
8 | -0.0010376 | 1.0247e-33 | 0.0010392 | 4.4081e-28 | 1.5869e-06 | 4.4081e-28 | 0.0017143 | 0.0017143 | 0.0017143 | 0.99847 | -2.4303e-23 | 1 | 0 | 8.6929
9 | -0.0010376 | 1.0247e-33 | 0.0010392 | 4.4081e-28 | 1.5869e-06 | 4.4081e-28 | 0.0017143 | 0.0017143 | 0.0017143 | 0.99847 | -2.4303e-23 | 1 | 0 | 8.6929
10 | -0.001 | 8.8385e-34 | 0.0010015 | 4.0937e-28 | 1.4737e-06 | 4.0937e-28 | 0.001652 | 0.001652 | 0.001652 | 0.99853 | -2.342e-23 | 1 | 0 | 8.3772

## res_ext_grid
| p_mw | q_mvar
0 | -0.0092771 | 0

## res_load
| p_mw | q_mvar
4 | 0.002 | 0
11 | 0.0005 | 0
3 | 0.001 | 0
1 | 0.0005 | 0
2 | 0.0005 | 0

## res_sgen
| p_mw | q_mvar
0 | 0.03 | 0
1 | 0.03 | 0

## res_storage
| p_mw | q_mvar
0 | 0 | 0
1 | 0.011 | 0
2 | 0.022 | 0

## converter
| name | from_bus | to_bus | type | P | efficiency | stand_by_loss | efficiency curve | droop_curve | conv_rank | converter_catalogue
0 | Conv_1 | 0 | 1 | AC/DC Converter Non-Isolated | 0.1 | [[ 10. 0.93 ] [ 30. 0.96 ] [ 60. 0.975] [100. 0.975]] | 0.00085 | [[0,100],[50,98],[75,97],[100,95]] | [[1.025 0. ] [1. 1. ] [1. 1. ] [1. 1. ] [1. 1. ] [0.975 1. ]] | 0 | Unnamed: 0 Converter type Ecosystem Stand-by losses (W) \ 0 NaN AC/DC Converter Non-Isolated ODCA 850 1 NaN AC/DC Converter Non-Isolated ODCA 1000 2 NaN AC/DC Converter Non-Isolated ODCA 1250 3 NaN AC/DC Converter Non-Isolated ODCA 1500 Voltage level V1 (V) Voltage level V2 (V) Nominal power (kW) \ 0 400 700 100 1 400 700 125 2 400 700 150 3 400 700 175 Efficiency max (%) \ 0 0.975 1 0.975 2 0.975 3 0.975 Efficiency curve [Xi;Yi], i={1,2,3,4}, \nwith X= Factor of Nominal Power (%), Y=Efficiency (%) \ 0 [10;93], [30; 96], [60; 97.5], [100; 97.5] 1 [10;93], [30; 96], [60; 97.5], [100; 97.5] 2 [10;93], [30; 96], [60; 97.5], [100; 97.5] 3 [10;93], [30; 96], [60; 97.5], [100; 97.5] Approximate cost (kEUR) Product carbon footprint Weight (kg) \ 0 17.0 NaN NaN 1 NaN NaN NaN 2 NaN NaN NaN 3 NaN NaN NaN Reliability index 0 20-year lifetime 1 NaN 2 NaN 3 NaN
1 | Conv_2 | 3 | 4 | Storage DC/DC Converter | 0.04 | [[ 4. 0.93 ] [12. 0.96 ] [24. 0.975] [40. 0.975]] | 0.0005 | [[0,100],[50,98],[75,97],[100,95]] | [[ 1.2 1. ] [ 1.005 0. ] [ 1. 0. ] [ 1. 0. ] [ 0.995 0. ] [ 0.8 -1. ]] | 2 | Unnamed: 0 Converter type Ecosystem Stand-by losses (W) \ 0 NaN Storage DC/DC Converter ODCA 500 1 NaN Storage DC/DC Converter ODCA 500 2 NaN Storage DC/DC Converter ODCA 500 3 NaN Storage DC/DC Converter ODCA 500 Voltage level V1 (V) Voltage level V2 (V) Nominal power (kW) \ 0 700 150 20 1 700 150 30 2 700 150 40 3 700 150 50 Efficiency max (%) \ 0 0.975 1 0.975 2 0.975 3 0.975 Efficiency curve [Xi;Yi], i={1,2,3,4}, \nwith X= Factor of Nominal Power (%), Y=Efficiency (%) \ 0 [10;93], [30; 96], [60; 97.5], [100; 97.5] 1 [10;93], [30; 96], [60; 97.5], [100; 97.5] 2 [10;93], [30; 96], [60; 97.5], [100; 97.5] 3 [10;93], [30; 96], [60; 97.5], [100; 97.5] Approximate cost (kEUR) Product carbon footprint Weight (kg) \ 0 NaN NaN NaN 1 NaN NaN NaN 2 NaN NaN NaN 3 NaN NaN NaN Reliability index 0 NaN 1 NaN 2 NaN 3 NaN
2 | Conv_3 | 5 | 6 | EV DC/DC Converter | 0.014 | [[ 1.4 0.93 ] [ 4.2 0.96 ] [ 8.4 0.975] [14. 0.975]] | 0.0005 | [[0,100],[50,98],[75,97],[100,95]] | [[1.025 1. ] [1. 1. ] [1. 1. ] [0.985 1. ] [0.97 0. ]] | 1 | Unnamed: 0 Converter type Ecosystem Stand-by losses (W) \ 0 NaN EV DC/DC Converter ODCA 500 1 NaN EV DC/DC Converter ODCA 500 2 NaN EV DC/DC Converter ODCA 500 3 NaN EV DC/DC Converter ODCA 500 Voltage level V1 (V) Voltage level V2 (V) Nominal power (kW) \ 0 700 150 9 1 700 150 14 2 700 150 24 3 700 150 36 Efficiency max (%) \ 0 0.975 1 0.975 2 0.975 3 0.975 Efficiency curve [Xi;Yi], i={1,2,3,4}, \nwith X= Factor of Nominal Power (%), Y=Efficiency (%) \ 0 [10;93], [30; 96], [60; 97.5], [100; 97.5] 1 [10;93], [30; 96], [60; 97.5], [100; 97.5] 2 [10;93], [30; 96], [60; 97.5], [100; 97.5] 3 [10;93], [30; 96], [60; 97.5], [100; 97.5] Approximate cost (kEUR) Product carbon footprint Weight (kg) \ 0 NaN NaN NaN 1 NaN NaN NaN 2 NaN NaN NaN 3 NaN NaN NaN Reliability index 0 NaN 1 NaN 2 NaN 3 NaN
3 | Conv_4 | 7 | 8 | EV DC/DC Converter | 0.036 | [[ 3.6 0.93 ] [10.8 0.96 ] [21.6 0.975] [36. 0.975]] | 0.0005 | [[0,100],[50,98],[75,97],[100,95]] | [[1.025 1. ] [1. 1. ] [1. 1. ] [0.986 1. ] [0.971 0. ]] | 3 | Unnamed: 0 Converter type Ecosystem Stand-by losses (W) \ 0 NaN EV DC/DC Converter ODCA 500 1 NaN EV DC/DC Converter ODCA 500 2 NaN EV DC/DC Converter ODCA 500 3 NaN EV DC/DC Converter ODCA 500 Voltage level V1 (V) Voltage level V2 (V) Nominal power (kW) \ 0 700 150 9 1 700 150 14 2 700 150 24 3 700 150 36 Efficiency max (%) \ 0 0.975 1 0.975 2 0.975 3 0.975 Efficiency curve [Xi;Yi], i={1,2,3,4}, \nwith X= Factor of Nominal Power (%), Y=Efficiency (%) \ 0 [10;93], [30; 96], [60; 97.5], [100; 97.5] 1 [10;93], [30; 96], [60; 97.5], [100; 97.5] 2 [10;93], [30; 96], [60; 97.5], [100; 97.5] 3 [10;93], [30; 96], [60; 97.5], [100; 97.5] Approximate cost (kEUR) Product carbon footprint Weight (kg) \ 0 NaN NaN NaN 1 NaN NaN NaN 2 NaN NaN NaN 3 NaN NaN NaN Reliability index 0 NaN 1 NaN 2 NaN 3 NaN
4 | Conv_5 | 9 | 11 | PV DC/DC Converter | 0.04 | [[ 4. 0.93 ] [12. 0.96 ] [24. 0.975] [40. 0.975]] | 0.0005 | [[0,100],[50,98],[75,97],[100,95]] | [[1.025 1. ] [1. 1. ] [1. 1. ] [1. 1. ] [1. 1. ] [0.975 1. ]] | 2 | Unnamed: 0 Converter type Ecosystem Stand-by losses (W) \ 0 NaN PV DC/DC Converter ODCA 500 1 NaN PV DC/DC Converter ODCA 500 2 NaN PV DC/DC Converter ODCA 500 3 NaN PV DC/DC Converter ODCA 500 Voltage level V1 (V) Voltage level V2 (V) Nominal power (kW) \ 0 700 150 20 1 700 150 30 2 700 150 40 3 700 150 50 Efficiency max (%) \ 0 0.975 1 0.975 2 0.975 3 0.975 Efficiency curve [Xi;Yi], i={1,2,3,4}, \nwith X= Factor of Nominal Power (%), Y=Efficiency (%) \ 0 [10;93], [30; 96], [60; 97.5], [100; 97.5] 1 [10;93], [30; 96], [60; 97.5], [100; 97.5] 2 [10;93], [30; 96], [60; 97.5], [100; 97.5] 3 [10;93], [30; 96], [60; 97.5], [100; 97.5] Approximate cost (kEUR) Product carbon footprint Weight (kg) \ 0 NaN NaN NaN 1 NaN NaN NaN 2 NaN NaN NaN 3 NaN NaN NaN Reliability index 0 NaN 1 NaN 2 NaN 3 NaN
5 | Conv_6 | 10 | 11 | PV DC/DC Converter | 0.04 | [[ 4. 0.93 ] [12. 0.96 ] [24. 0.975] [40. 0.975]] | 0.0005 | [[0,100],[50,98],[75,97],[100,95]] | [[1.025 1. ] [1. 1. ] [1. 1. ] [1. 1. ] [1. 1. ] [0.975 1. ]] | 2 | Unnamed: 0 Converter type Ecosystem Stand-by losses (W) \ 0 NaN PV DC/DC Converter ODCA 500 1 NaN PV DC/DC Converter ODCA 500 2 NaN PV DC/DC Converter ODCA 500 3 NaN PV DC/DC Converter ODCA 500 Voltage level V1 (V) Voltage level V2 (V) Nominal power (kW) \ 0 700 150 20 1 700 150 30 2 700 150 40 3 700 150 50 Efficiency max (%) \ 0 0.975 1 0.975 2 0.975 3 0.975 Efficiency curve [Xi;Yi], i={1,2,3,4}, \nwith X= Factor of Nominal Power (%), Y=Efficiency (%) \ 0 [10;93], [30; 96], [60; 97.5], [100; 97.5] 1 [10;93], [30; 96], [60; 97.5], [100; 97.5] 2 [10;93], [30; 96], [60; 97.5], [100; 97.5] 3 [10;93], [30; 96], [60; 97.5], [100; 97.5] Approximate cost (kEUR) Product carbon footprint Weight (kg) \ 0 NaN NaN NaN 1 NaN NaN NaN 2 NaN NaN NaN 3 NaN NaN NaN Reliability index 0 NaN 1 NaN 2 NaN 3 NaN
6 | Conv_7 | 12 | 13 | PDU DC/DC Converter Non-Isolated | 0.009 | [[0.9 0.93 ] [2.7 0.96 ] [5.4 0.975] [9. 0.975]] | 0.0005 | [[0,100],[50,98],[75,97],[100,95]] | [[1.025 1. ] [1. 1. ] [1. 1. ] [0.98 1. ] [0.95 0. ]] | 0 | Unnamed: 0 Converter type Ecosystem Stand-by losses (W) \ 0 NaN PDU DC/DC Converter Non-Isolated ODCA 500 1 NaN PDU DC/DC Converter Non-Isolated ODCA 500 2 NaN PDU DC/DC Converter Non-Isolated ODCA 500 3 NaN PDU DC/DC Converter Non-Isolated ODCA 500 Voltage level V1 (V) Voltage level V2 (V) Nominal power (kW) \ 0 350 48 9 1 350 48 14 2 350 48 24 3 350 48 36 Efficiency max (%) \ 0 0.975 1 0.975 2 0.975 3 0.975 Efficiency curve [Xi;Yi], i={1,2,3,4}, \nwith X= Factor of Nominal Power (%), Y=Efficiency (%) \ 0 [10;93], [30; 96], [60; 97.5], [100; 97.5] 1 [10;93], [30; 96], [60; 97.5], [100; 97.5] 2 [10;93], [30; 96], [60; 97.5], [100; 97.5] 3 [10;93], [30; 96], [60; 97.5], [100; 97.5] Approximate cost (kEUR) Product carbon footprint Weight (kg) \ 0 NaN NaN NaN 1 NaN NaN NaN 2 NaN NaN NaN 3 NaN NaN NaN Reliability index 0 NaN 1 NaN 2 NaN 3 NaN
7 | Conv_8 | 14 | 15 | PDU DC/DC Converter Non-Isolated | 0.009 | [[0.9 0.93 ] [2.7 0.96 ] [5.4 0.975] [9. 0.975]] | 0.0005 | [[0,100],[50,98],[75,97],[100,95]] | [[1.025 1. ] [1. 1. ] [1. 1. ] [0.978 1. ] [0.945 0. ]] | 0 | Unnamed: 0 Converter type Ecosystem Stand-by losses (W) \ 0 NaN PDU DC/DC Converter Non-Isolated ODCA 500 1 NaN PDU DC/DC Converter Non-Isolated ODCA 500 2 NaN PDU DC/DC Converter Non-Isolated ODCA 500 3 NaN PDU DC/DC Converter Non-Isolated ODCA 500 Voltage level V1 (V) Voltage level V2 (V) Nominal power (kW) \ 0 350 48 9 1 350 48 14 2 350 48 24 3 350 48 36 Efficiency max (%) \ 0 0.975 1 0.975 2 0.975 3 0.975 Efficiency curve [Xi;Yi], i={1,2,3,4}, \nwith X= Factor of Nominal Power (%), Y=Efficiency (%) \ 0 [10;93], [30; 96], [60; 97.5], [100; 97.5] 1 [10;93], [30; 96], [60; 97.5], [100; 97.5] 2 [10;93], [30; 96], [60; 97.5], [100; 97.5] 3 [10;93], [30; 96], [60; 97.5], [100; 97.5] Approximate cost (kEUR) Product carbon footprint Weight (kg) \ 0 NaN NaN NaN 1 NaN NaN NaN 2 NaN NaN NaN 3 NaN NaN NaN Reliability index 0 NaN 1 NaN 2 NaN 3 NaN
8 | Conv_9 | 16 | 17 | PDU DC/DC Converter Non-Isolated | 0.009 | [[0.9 0.93 ] [2.7 0.96 ] [5.4 0.975] [9. 0.975]] | 0.0005 | [[0,100],[50,98],[75,97],[100,95]] | [[1.025 1. ] [1. 1. ] [1. 1. ] [0.976 1. ] [0.941 0. ]] | 0 | Unnamed: 0 Converter type Ecosystem Stand-by losses (W) \ 0 NaN PDU DC/DC Converter Non-Isolated ODCA 500 1 NaN PDU DC/DC Converter Non-Isolated ODCA 500 2 NaN PDU DC/DC Converter Non-Isolated ODCA 500 3 NaN PDU DC/DC Converter Non-Isolated ODCA 500 Voltage level V1 (V) Voltage level V2 (V) Nominal power (kW) \ 0 350 48 9 1 350 48 14 2 350 48 24 3 350 48 36 Efficiency max (%) \ 0 0.975 1 0.975 2 0.975 3 0.975 Efficiency curve [Xi;Yi], i={1,2,3,4}, \nwith X= Factor of Nominal Power (%), Y=Efficiency (%) \ 0 [10;93], [30; 96], [60; 97.5], [100; 97.5] 1 [10;93], [30; 96], [60; 97.5], [100; 97.5] 2 [10;93], [30; 96], [60; 97.5], [100; 97.5] 3 [10;93], [30; 96], [60; 97.5], [100; 97.5] Approximate cost (kEUR) Product carbon footprint Weight (kg) \ 0 NaN NaN NaN 1 NaN NaN NaN 2 NaN NaN NaN 3 NaN NaN NaN Reliability index 0 NaN 1 NaN 2 NaN 3 NaN
9 | Conv_10 | 18 | 19 | PDU DC/DC Converter Isolated | 0.009 | [[0.9 0.916] [2.7 0.955] [5.4 0.96 ] [9. 0.965]] | 0.0005 | [[0,100],[50,98],[75,97],[100,95]] | [[1.025 1. ] [1. 1. ] [1. 1. ] [1. 1. ] [1. 1. ] [0.975 0. ]] | 0 | Unnamed: 0 Converter type Ecosystem Stand-by losses (W) \ 0 NaN PDU DC/DC Converter Isolated ODCA 500 1 NaN PDU DC/DC Converter Isolated ODCA 500 2 NaN PDU DC/DC Converter Isolated ODCA 500 3 NaN PDU DC/DC Converter Isolated ODCA 500 Voltage level V1 (V) Voltage level V2 (V) Nominal power (kW) \ 0 700 350 9 1 700 350 14 2 700 350 24 3 700 350 36 Efficiency max (%) \ 0 0.96525 1 0.96525 2 0.96525 3 0.96525 Efficiency curve [Xi;Yi], i={1,2,3,4}, \nwith X= Factor of Nominal Power (%), Y=Efficiency (%) \ 0 [10;91.6], [30; 95.5], [60; 96], [100; 96.5] 1 [10;91.6], [30; 95.5], [60; 96], [100; 96.5] 2 [10;91.6], [30; 95.5], [60; 96], [100; 96.5] 3 [10;91.6], [30; 95.5], [60; 96], [100; 96.5] Approximate cost (kEUR) Product carbon footprint Weight (kg) \ 0 NaN NaN NaN 1 NaN NaN NaN 2 NaN NaN NaN 3 NaN NaN NaN Reliability index 0 NaN 1 NaN 2 NaN 3 NaN

## res_converter
| p_mw | loading (%) | pl_mw
0 | -0.0092771 | -10.8741 | -0.0015969
1 | 0.0005 | 0 | -0.0005
2 | 0.011782 | 78.5714 | -0.00078205
3 | 0.023064 | 61.1111 | -0.0010641
4 | -0.02875 | -75 | -0.00125
5 | -0.02875 | -75 | -0.00125
6 | 0.0010376 | 5.5556 | -0.00053763
7 | 0.0010376 | 5.5556 | -0.00053763
8 | 0.0010376 | 5.5556 | -0.00053763
9 | 0.0048014 | 45.7682 | -0.00068226

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | load | droop_curve | object
16 | load | p_nom_mw | object
17 | load | power_profile | object
18 | load | default_power_profile | object
19 | sgen | name | object
20 | sgen | bus | int64
21 | sgen | p_mw | float64
22 | sgen | q_mvar | float64
23 | sgen | sn_mva | float64
24 | sgen | scaling | float64
25 | sgen | in_service | bool
26 | sgen | type | object
27 | sgen | current_source | bool
28 | sgen | p_nom_mw | object
29 | sgen | power_profile | object
30 | sgen | default_power_profile | object
31 | storage | name | object
32 | storage | bus | int64
33 | storage | p_mw | float64
34 | storage | q_mvar | float64
35 | storage | sn_mva | float64
36 | storage | soc_percent | float64
37 | storage | min_e_mwh | float64
38 | storage | max_e_mwh | float64
39 | storage | scaling | float64
40 | storage | in_service | bool
41 | storage | type | object
42 | storage | p_nom_mw | object
43 | storage | power_profile | object
44 | storage | default_power_profile | object
45 | ext_grid | name | object
46 | ext_grid | bus | uint32
47 | ext_grid | vm_pu | float64
48 | ext_grid | va_degree | float64
49 | ext_grid | slack_weight | float64
50 | ext_grid | in_service | bool
51 | line | name | object
52 | line | std_type | object
53 | line | from_bus | uint32
54 | line | to_bus | uint32
55 | line | length_km | float64
56 | line | r_ohm_per_km | float64
57 | line | x_ohm_per_km | float64
58 | line | c_nf_per_km | float64
59 | line | g_us_per_km | float64
60 | line | max_i_ka | float64
61 | line | df | float64
62 | line | parallel | uint32
63 | line | type | object
64 | line | in_service | bool
65 | line | cable_rank | float64
66 | line | section | float64
67 | res_bus | vm_pu | float64
68 | res_bus | va_degree | float64
69 | res_bus | p_mw | float64
70 | res_bus | q_mvar | float64
71 | res_line | p_from_mw | float64
72 | res_line | q_from_mvar | float64
73 | res_line | p_to_mw | float64
74 | res_line | q_to_mvar | float64
75 | res_line | pl_mw | float64
76 | res_line | ql_mvar | float64
77 | res_line | i_from_ka | float64
78 | res_line | i_to_ka | float64
79 | res_line | i_ka | float64
80 | res_line | vm_from_pu | float64
81 | res_line | va_from_degree | float64
82 | res_line | vm_to_pu | float64
83 | res_line | va_to_degree | float64
84 | res_line | loading_percent | float64
85 | res_ext_grid | p_mw | float64
86 | res_ext_grid | q_mvar | float64
87 | res_load | p_mw | float64
88 | res_load | q_mvar | float64
89 | res_sgen | p_mw | float64
90 | res_sgen | q_mvar | float64
91 | res_storage | p_mw | float64
92 | res_storage | q_mvar | float64
93 | converter | name | object
94 | converter | from_bus | int64
95 | converter | to_bus | int64
96 | converter | type | object
97 | converter | P | float64
98 | converter | efficiency | object
99 | converter | stand_by_loss | float64
100 | converter | efficiency curve | object
101 | converter | droop_curve | object
102 | converter | conv_rank | int64
103 | converter | converter_catalogue | object
104 | res_converter | p_mw | float64
105 | res_converter | loading (%) | float64
106 | res_converter | pl_mw | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.10 | 2.14.0 | FALSE | FALSE |  | 50 | 1